## Slide 1: Reaching 98.5 % availability at 10k–500k NPUs: where we stand and what it takes
Goal: A_op ≥ 98.5 % per 30-day window for one synchronous training job — met nominally, with every mechanism derated, and in ≥ 90 % of windows. Four topologies: native Atlas 950 (1,024-NPU SuperPoD), SuperPoD Flex / UBL128, Atlas 900 A3 / CloudMatrix384, Atlas 800T A3 servers + RoCE.
Chart: Availability today (derated, %) by scale, four topologies — dashed line = goal 98.5 %
| 10k | 100k | 200k | 500k
Native 950 | 99.91 | 99.11 | 98.23 | 95.7
UBL128 | 99.91 | 99.15 | 98.32 | 95.91
CM384 | 99.9 | 98.98 | 97.98 | 95.1
800T A3 | 99.9 | 99.01 | 98.03 | 95.22
Goal 98.5 % | 98.5 | 98.5 | 98.5 | 98.5
36–39 min
MTBF today at 500k; MTTR 96–104 s
≥ 2.0–2.3 h
MTBF required at today’s MTTR (or MTTR ≤ 27–31 s)
39–41 s
MTTR of the recommended design (MTBF 45–48 min) — the gap closes mostly through MTTR
What it takes at each scale
1
Today’s gap
200k is just short (98.0–98.3 % derated; only 19–60 % of windows meet the goal). 500k is far off (95.1–95.9 %; no window meets it).
2
10k and 100k — nothing to change
Goal met today (10k 99.9 %, 100k 99.0–99.3 %). Hardware acceptance ceilings: ×11–14 of today’s failure rates at 10k, ×1.1–1.4 at 100k.
3
200k — recovery-process targets, no hardware change
Manual recovery 2 h → 30 min (950, UBL128). CM384 and 800T A3 also need the automatic attempt 180 → 60 s plus two mechanisms (C-LOSSLESS, D-HARD).
4
500k — mechanisms + recovery targets + hardware
Add D-HARD, D-RECOVERY-CLASSIFY, R-LINK-LOCAL, H-CONTROL-CONTINUITY; both recovery targets; failure rates ×0.75–0.87 (13–25 % better). Result: 99.3 % nominal / 98.5 % derated, 100 % of windows.
Notes: Basis: A_op = operational availability (30-day window, one synchronous training job); derated = every mechanism at coverage −5 pt, success −8 pt, times ×1.5; data from docs/backup/ascend-allocation/results.json.

## Slide 2: Where the 1.5-point budget goes — and the decisions we need
HAC-D allocation: layer budgets by fault unit; the least-effort mix of mechanisms, recovery levers and ARINC hardware; checked nominal, derated and per window. Details in the Findings volumes (Tables 1–7).
A
Layers: where the budget goes
B
Mechanisms: what each one buys
C
Topology: counts differ, rates barely
Chart: 1.50-pt budget at 500k by layer (native 950, derated)
| Cluster services 0.66 | NPU 0.37 | Node 0.21 | Cabinet 0.16 | SuperPoD + scale-out 0.02 | Other classes 0.09
U | 0.66 | 0.37 | 0.21 | 0.16 | 0.025 | 0.09
Allowed MTBF per instance at 500k: SuperPoD 1.7 y (950) / 3.0 y (CM384) / 49 y (UBL128); cabinet 15–18 y; node 26 y; NPU 78–91 y.
Chart: A_op gain at 500k, points (Shapley, native 950)
| R-ELASTIC | R-PROCESS | R-REPLAY | D-RECOVERY-CLASSIFY | R-LINK-LOCAL | R-RUNTIME-SNAPSHOT | H-CONTROL-CONTINUITY | C-LOSSLESS
Shapley | 2.93 | 1.36 | 1.09 | 1.06 | 0.45 | 0.42 | 0.35 | 0.34
23 ReMAP mechanisms → 7 kept for A_op, 5 for goodput only, 5 pruned. All 23 together reach 98.3 % at 500k — not enough on their own.
Failure rate per NPU is within 12 % across 18 designs (3,021–3,384 FIT); fabric and scale-out make up 1–5 % of it.
So the plan is the same on every topology; the topology sets the acceptance value per instance (SuperPoD, cabinet, node).
UB switch chips per 1,000 NPUs: CM384 1,167 · native 950 1,141 · 800T A3 875 · UBL128 31.
Decisions requested
1
Adopt the mechanism set and recovery targets for ≥ 200k
Manual recovery ≤ 30 min, automatic attempt ≤ 60 s; the four added mechanisms at 500k.
2
Issue hardware acceptance values for 500k procurement
Per unit, from Findings Table 3 — e.g. NPU module ≤ 1,257–1,463 FIT (today 1,677).
3
Validate the failure-rate basis with fleet data
Values are GPU-fleet analogues per unit; a measurement plan before decisions above 200k.
4
Fund HAC-D v5: the report pipeline
New topology / library values / scales → a Findings report natively (PLAN_V5_REPORT_PIPELINE.md).
Notes: Budget, mechanism and topology figures come from Findings Tables 2 and 7 and BOM Table 3; acceptance values per unit are in each Findings Table 3.